## DHW
DHW_Service | 1 | - | If you want to model the domestic hot water service, choose the value '1'. If no domestic hot water service is available, choose '0'.
COPDHW | 2.82 | - | Heat pump COP for domestic hot water service according EN 16147.
t_DHW_heatup | 6180 | s | Domestic hot water storage heat-up time from 10 °C until thermostat switch-off at temperature T_DHW_ref according EN 16147.
T_DHW_ref | 55 | °C | Domestic hot water storage thermostat switch-off temperature according EN 16147.
T_DHWmax1 | 55 | °C | Maximum domestic hot water supply temperature without back-up heater operation (Flex1). Please make sure that Tcomp3 = T_SHmax1 = T_DHWmax1
T_DHWmax2 | 60 | °C | Maximum domestic hot water supply temperature with back-up heater operation (Flex2). If BUH_service=0, T_SHmax2 will equal T_SHmax1.
V_TES_DHW | 180 | l | Thermal energy storage size for domestic hot water service.
QlossDHW | 1.2 | kWh/24h | Standing losses of thermal energy storage for domestic hot water service.
E_DHW_Profile_extraction_24h | 11.66 | kWh | Extracted domestic hot water energy according EN 16147 tapping profile.
tfactorDHW_reducedday | 875 | minutes | Total time between the start of the first and end of the last domestic hot water draw-off according the EN 16147 profile.

## BUH
BUH_service | 1 | - | If you want to model the back-up heater availability, choose the value '1'. If no back-up heater is available, choose '0'.
BUH_simultaneous_SH | 0 | - | Select '1' if the back-up heater operates in series with the compressor during space heating service or select '0' if the back-up heater only operates after compressor switch off.
BUH_simultaneous_DHW | 0 | - | Select '1' if the back-up heater operates in series with the compressor during domestic hot water service or select '0' if the back-up heater only operates after compressor switch off.
PBUH | 3000 | W | Nominal back-up heater power.
PBUHmin | 1000 | W | Minimum back-up heater power.

## SH
Q35rated | 6000 | W | Rated/nominal space heating power for an average European climate at a space heating water supply temperature of 35 °C.
V_TES_SH | 200 | l | Thermal energy storage size for space heating service.
T_SHmax1 | 55 | °C | Maximum space heating supply temperature without back-up heater operation (Flex1). Please make sure that Tcomp3 = T_SHmax1 = T_DHWmax1
T_SHmax2 | 65 | °C | Maximum space heating supply temperature with back-up heater operation (Flex2). If BUH_service=0, T_SHmax2 will equal T_SHmax1.
QlossSH | 1.46 | kWh/24h | Standing losses of thermal energy storage for space heating service.
COP35SH_88 | 4.84 | - | Heat pump COP at a space heating supply temperature of 35 °C at an outdoor temperature of -7 °C.
COP35SH_54 | 5.36 | - | Heat pump COP at a space heating supply temperature of 35 °C at an outdoor temperature of 2 °C.
COP35SH_35 | 5.42 | - | Heat pump COP at a space heating supply temperature of 35 °C at an outdoor temperature of 7 °C.
COP35SH_15 | 4.57 | - | Heat pump COP at a space heating supply temperature of 35 °C at an outdoor temperature of 12 °C.

## General
timestep | 5 | s | Select your preferred time step (recommended time step is five seconds for accuracy reasons).
casenumber | 1 | - | This variable can be used to number your cases. Please, only use numbers.
separated_folder | 0 | - | If you want to store the results in a folder of your choice (specified in next variable 'filelocation'), choose '1', else choose '0' to store the results in your default Python directory.
filelocation | C:\\Users\\Documents\\ | - | Provide the full path of your preferred result folder.